## Glossary
Buses | Description | Typical numbers
bus_n | Bus number
vn_kv | Bus rated voltage [kV] (ph-ph or sqrt(3)*En where En is equal to 1p.u. reference voltage)
earth_r_ohm | Neutral grounding resistance [ohm] | 1*10 -10 ÷ 1*10 10
phase_n | Number of phases per each node
name | Original bus numbering (for reference)
x | Bus x-coordinate in graph
y | Bus y-coordinate in graph
gr_ph_n | Phase at which grounding resistance is connected, The value "0" means that no phase is considered as grounding neutral point and grounding resistance is not connected.
Wiredata | Description | Typical numbers
wire_n | Identifies the type. Progressive and univoque number.
diam_m | Diameter [m] | ÷
gmr | Coefficient for GMR calculation | 0,7 ÷ 1
rc_ohm | DC conductor resistance [ohm/km] | ÷
g_s | conductor conductance [S/km] | 0
max_i_ka | Maximum admitted current [kA] | ÷
Configurations | Description | Typical numbers
cfg_n | Configuration number. Progressive number, that must univocally refer to a wire configuration between "Configurations", "Cfg_sq" and "Configurations_mat" sheets.
phase | Phase number | (1,…, 4)
wire_n | Type of conductor (univoque ref to wiredata)
x_m | Horizontal coordinate of respective phase [m]
y_m | Vertical coordinate of respective phase [m]
Configurations_mat | Description | Typical numbers
cfg_n | Configuration number. Progressive number, that must univocally refer to a wire configuration between "Configurations", "Cfg_sq" and "Configurations_mat" sheets.
phase | Phase number | (1,…, 4)
max_i_ka | Maximum admitted current [kA] | ÷
ph1_r_ohm_per_km
ph1_x_ohm_per_km
ph2_r_ohm_per_km
ph2_x_ohm_per_km
ph3_r_ohm_per_km
ph3_x_ohm_per_km
ph4_r_ohm_per_km
ph4_x_ohm_per_km
ph1_g_siemens_per_km
ph1_b_siemens_per_km
ph2_g_siemens_per_km
ph2_b_siemens_per_km
ph3_g_siemens_per_km
ph3_b_siemens_per_km
ph4_g_siemens_per_km
ph4_b_siemens_per_km
Cfg_sq | Description | Typical numbers
cfg_n | Configuration number. Progressive number, that must univocally refer to a wire configuration between "Configurations", "Cfg_sq" and "Configurations_mat" sheets.
r_ohm_per_km | Phase number | (1,…, 4)
x_ohm_per_km
r0_ohm_per_km
x0_ohm_per_km
c_nf_per_km
c0_nf_per_km
max_i_ka | Maximum admitted current [kA] | ÷
Lines | Description | Typical numbers
from_bus | Sending bus number
from_bus_terms | Sending bus phases (terms considered must be equal to the line conductors number). The value must be a string and phases number must be separated by a "_" | "1_2_3" for a standard 3-wire line or "1_2_3_4" for a standard 4-wire line
to_bus | Receiving bus number
to_bus_terms | Receiving bus phases (terms considered must be equal to the line conductors number). The value must be a string and phases number must be separated by a "_" | "1_2_3" for a standard 3-wire line or "1_2_3_4" for a standard 4-wire line
std_type | Configuration type (w ref to Configurations)
length_km | Length
name | Original line numbering (for reference)
Transformers | Description | Typical numbers
hv_bus | Sending bus number
lv_bus | Receiving bus number
vn_hv_kv | Rated primary voltage [kV]
vn_lv_kv | Rated secondary voltage [kV]
sn_mva | Rated apparent power [MVA]
vk_percent | Short-circuit voltage in percent
vkr_percent | Short-circuit power in percent
pfe_kw | Open circuit power losses [kW]
i0_percent | Open circuit current in percent
conn1 | Primary connection type | 1 – Wye
2 – Delta
conn2 | Secondary connection type | 1 – Wye
2 – Delta
group | Transformer group | 0 ÷ 12
tap_step_percent | Voltage change per tap in percent | e.g. 2.5
tap_pos | Actual tap position | e.g. 0
tap_max | Maximum tap position | e.g. 4
tap_min | Minimum tap position | e.g. -4
vrif_pu | Voltage reference for OLTC in p.u. | 0 means NO-OLTC, or OLTC out of service
db_percent | Deadband width in percent | e.g. 3
oltc_bus | Controlled bus for tap adjustment
r_ohm | Equivalent resistance for LDC
x_ohm | Equivalent reactance for LDC
synchro | OLTC control options | 1 – Phase-synchronous
2 – Phase-decoupled
1phTransformers | Description | Typical numbers
tr_n | Transformer number. Rows wth same tr_n number define coils of the same transformer.
circ_n | Coil number. For each winding multiple coils can be defined (e.g. a 2-winding standard 3-phase transformer is made of 3 coils hv-side and 3 coils lv-side)
bus_n | Bus number of each winding
from_ph | Coil sending phase number (winding bus number is already defined with bus_n)
to_ph | Coil receiving phase number (winding bus number is already defined with bus_n)
vn_kv | Coil rated voltage [kV]
sn_mva | Coil rated apparent power [MVA]
vk_percent | Coil short-circuit voltage in percent
vkr_percent | Coil short-circuit power in percent
pfe_kw | Coil open circuit losses [kW]
i0_percent | Open circuit current in percent
tap_step_percent | Voltage change per tap in percent | e.g. 2.5
tap_pos | Actual tap position | e.g. 0
tap_max | Maximum tap position | e.g. 4
tap_min | Minimum tap position | e.g. -4
vrif_pu | Voltage reference for OLTC in p.u. | 0 means NO-OLTC, or OLTC out of service
db_percent | Deadband width in percent | e.g. 3
oltc_bus | Controlled bus for tap adjustment
r_ohm | Equivalent resistance for LDC
x_ohm | Equivalent reactance for LDC
synchro | OLTC control options | 1 – Phase-synchronous
2 – Phase-decoupled
Loads | Descrizione | Typical numbers
bus | Connection bus number
phase | Field enabled writing "1" or 2 under "conn" field. Connection phase at bus
p_mw | Active rated power [MW]
q_mvar | Reactive rated power [MVar]
conn | Connection type | 1 – Wye connected. Enables "phase" field
2 – Delta connected. Enables "phase" field
3 - Enables "from-ph" and "to_ph" fields
kzp | Z-coefficient in ZIP model (active part) | 0 ÷ 1
kip | I-coefficient in ZIP model (active part) | 0 ÷ 1
kpp | P-coefficient in ZIP model (active part) | 0 ÷ 1
kzq | Z-coefficient in ZIP model (reactive part) | 0 ÷ 1
kiq | I-coefficient in ZIP model (reactive part) | 0 ÷ 1
kpq | P-coefficient in ZIP model (reactive part) | 0 ÷ 1
custom
from_ph | Field enabled writing "3" under "conn" field. Phase at which the single element load is connected at one side. The value "0" means that the load is connected to the ground.
to_ph | Field enabled writing "3" under "conn" field. Phase at which the single element load is connected at the other side. The value "0" means that the load is connected to the ground.
type | Load type (string to be matched in the profiles set)
Generators | Descrizione | Typical numbers
bus | Connection bus number
phase | Field enabled writing "1" or 2 under "conn" field. Connection phase at bus
p_mw | Active rated power
q_mvar | Reactive rated power
conn | Connection type | 1 – Wye connected. Enables "phase" field
2 – Delta connected. Enables "phase" field
3 - Enables "from-ph" and "to_ph" fields
kzp | Z-coefficient in ZIP model (active part) | 0 ÷ 1
kip | I-coefficient in ZIP model (active part) | 0 ÷ 1
kpp | P-coefficient in ZIP model (active part) | 0 ÷ 1
kzq | Z-coefficient in ZIP model (reactive part) | 0 ÷ 1
kiq | I-coefficient in ZIP model (reactive part) | 0 ÷ 1
kpq | P-coefficient in ZIP model (reactive part) | 0 ÷ 1
custom
from_ph | Field enabled writing "3" under "conn" field. Phase at which the single element gen is connected at one side. The value "0" means that the gen is connected to the ground.
to_ph | Field enabled writing "3" under "conn" field. Phase at which the single element gen is connected at the other side. The value "0" means that the gen is connected to the ground.
type | Generator type (string to be matched in the profiles set)
P_profiles | Descrizione | Typical numbers
id | Progressive index number
| Active power measured profiles [p.u.] | each column has the load type in header
Q_profiles | Descrizione | Typical numbers
id | Progressive index number
| Reactive power measured profiles [p.u.] | each column has the load type in header
General_data | Descrizione | Typical numbers
Start_Date | Date (format dd/mm/yy)
Start_Time | Time (format 24h - hh:mm:ss)
Time step | Time interval (format 24h - hh:mm:ss)
End_Date | Date (format dd/mm/yy)
End_Time | Time (format 24h - hh:mm:ss)

## General_data
start_date | start_time | time_step | end_date | end_time | f_hz | rho_ohmm | sbase_mva | tol_vmag_pu | tol_vang_rad | max_iter
2022-01-01 | 0:00 | 1:00 | 2022-01-02 | 0:00 | 50 | 100 | 1 | 0.0001 | 0.0001 | 50

## Buses
bus_n | vn_kv | earth_r_ohm | phase_n | name | x | y | gr_ph_n
1 | 20 | 1e-10 | 4 | 0 | 0 | 0 | 4
2 | 0.4 | 1e-10 | 4 | 1 | 0 | 0 | 4
3 | 0.4 | 10000000000 | 4 | 3 | 0 | 0 | 4
4 | 0.4 | 10000000000 | 4 | 4 | 0 | 0 | 4
5 | 0.4 | 10000000000 | 4 | 6 | 0 | 0 | 4
6 | 0.4 | 10000000000 | 4 | 9 | 0 | 0 | 4
7 | 0.4 | 10000000000 | 4 | 10 | 0 | 0 | 4
8 | 0.4 | 10000000000 | 4 | 11 | 0 | 0 | 4
9 | 0.4 | 10000000000 | 4 | 14 | 0 | 0 | 4
10 | 0.4 | 10000000000 | 4 | 15 | 0 | 0 | 4
11 | 0.4 | 10000000000 | 4 | 16 | 0 | 0 | 4
12 | 0.4 | 10000000000 | 4 | 17 | 0 | 0 | 4
13 | 0.4 | 10000000000 | 4 | 18 | 0 | 0 | 4

## Wiredata
wire_n | diam_m | gmr | rc_ohm | g_s | max_i_ka
1 | 0.0175 | 0.76686 | 0.162 | 0 | 0.24
2 | 0.0138 | 0.76957 | 0.265 | 0 | 0.24
3 | 0.0124 | 0.76613 | 0.325 | 0 | 0.24
4 | 0.00564 | 0.78014 | 1.54 | 0 | 0.24
5 | 0.00668 | 0.77844 | 1.11 | 0 | 0.24
6 | 0.00944 | 0.77966 | 0.568 | 0 | 0.24
7 | 0.0051 | 0.7788 | 1.15 | 0 | 0.24

## Configurations
cfg_n | phase | wire_n | x_m | y_m
1 | 1 | 1 | 0.052 | 0.152
1 | 2 | 1 | 0 | 0.152
1 | 3 | 1 | 0.052 | 0.1
1 | 4 | 2 | 0 | 0.1
2 | 1 | 2 | 0.042 | 0.142
2 | 2 | 2 | 0 | 0.142
2 | 3 | 2 | 0.042 | 0.1
2 | 4 | 3 | 0 | 0.1
3 | 1 | 3 | 0.039 | 0.139
3 | 2 | 3 | 0 | 0.139
3 | 3 | 3 | 0.039 | 0.1
3 | 4 | 6 | 0 | 0.1
4 | 1 | 4 | 0.024 | 0.124
4 | 2 | 4 | 0 | 0.124
4 | 3 | 4 | 0.024 | 0.1
4 | 4 | 7 | 0 | 0.1
5 | 1 | 5 | 0.026 | 0.126
5 | 2 | 5 | 0 | 0.126
5 | 3 | 5 | 0.026 | 0.1
5 | 4 | 7 | 0 | 0.1
6 | 1 | 6 | 0.032 | 0.132
6 | 2 | 6 | 0 | 0.132
6 | 3 | 6 | 0.032 | 0.1
6 | 4 | 5 | 0 | 0.1

## Configurations_mat
cfg_n | phase | max_i_ka | ph1_r_ohm_per_km | ph1_x_ohm_per_km | ph2_r_ohm_per_km | ph2_x_ohm_per_km | ph3_r_ohm_per_km | ph3_x_ohm_per_km | ph4_r_ohm_per_km | ph4_x_ohm_per_km | ph1_g_siemens_per_km | ph1_b_siemens_per_km | ph2_g_siemens_per_km | ph2_b_siemens_per_km | ph3_g_siemens_per_km | ph3_b_siemens_per_km | ph4_g_siemens_per_km | ph4_b_siemens_per_km
601 | 1 | 1 | 0.21531 | 0.6325 | 0.096934 | 0.31174 | 0.098177 | 0.26321 | 0 | 0 | 0 | 3.9145e-06 | 0 | -1.2401e-06 | 0 | -7.8262e-07 | 0 | 0
601 | 2 | 1 | 0.096934 | 0.31174 | 0.20971 | 0.65107 | 0.095381 | 0.23917 | 0 | 0 | 0 | -1.2401e-06 | 0 | 3.7032e-06 | 0 | -4.6087e-07 | 0 | 0
601 | 3 | 1 | 0.098177 | 0.26321 | 0.095381 | 0.23917 | 0.21214 | 0.643 | 0 | 0 | 0 | -7.8262e-07 | 0 | -4.6087e-07 | 0 | 3.5037e-06 | 0 | 0
602 | 1 | 1 | 0.46765 | 0.73409 | 0.098177 | 0.26321 | 0.096934 | 0.23917 | 0 | 0 | 0 | 3.5412e-06 | 0 | -6.7214e-07 | 0 | -1.0504e-06 | 0 | 0
602 | 2 | 1 | 0.098177 | 0.26321 | 0.46448 | 0.74459 | 0.095381 | 0.23917 | 0 | 0 | 0 | -6.7214e-07 | 0 | 3.2184e-06 | 0 | -4.0936e-07 | 0 | 0
602 | 3 | 1 | 0.096934 | 0.23917 | 0.095381 | 0.23917 | 0.46205 | 0.75261 | 0 | 0 | 0 | -1.0504e-06 | 0 | -4.0936e-07 | 0 | 3.3707e-06 | 0 | 0
603 | 1 | 1 | 0.82605 | 0.83705 | 0.12838 | 0.28527 | 0 | 0 | 0 | 0 | 0 | 2.9265e-06 | 0 | -5.5917e-07 | 0 | 0 | 0 | 0
603 | 2 | 1 | 0.12838 | 0.28527 | 0.82257 | 0.84314 | 0 | 0 | 0 | 0 | 0 | -5.5917e-07 | 0 | 2.8992e-06 | 0 | 0 | 0 | 0
604 | 1 | 1 | 0.82257 | 0.84314 | 0.12838 | 0.28527 | 0 | 0 | 0 | 0 | 0 | 2.8992e-06 | 0 | -5.5917e-07 | 0 | 0 | 0 | 0
604 | 2 | 1 | 0.12838 | 0.28527 | 0.82605 | 0.83705 | 0 | 0 | 0 | 0 | 0 | -5.5917e-07 | 0 | 2.9807e-06 | 0 | 0 | 0 | 0
605 | 1 | 1 | 0.82593 | 0.8373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8082e-06 | 0 | 0 | 0 | 0 | 0 | 0
606 | 1 | 1 | 0.49598 | 0.27732 | 0.19834 | 0.020381 | 0.17703 | -0.0088856 | 0 | 0 | 0 | 6.0205e-05 | 0 | 0 | 0 | 0 | 0 | 0
606 | 2 | 1 | 0.19834 | 0.020381 | 0.49033 | 0.2511 | 0.19834 | 0.020381 | 0 | 0 | 0 | 0 | 0 | 6.0205e-05 | 0 | 0 | 0 | 0
606 | 3 | 1 | 0.17703 | -0.0088856 | 0.19834 | 0.020381 | 0.49598 | 0.27732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0205e-05 | 0 | 0
607 | 1 | 1 | 0.83419 | 0.31839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5297e-05 | 0 | 0 | 0 | 0 | 0 | 0
608 | 1 | 1 | 0.21531 | 0.6325 | 0.096934 | 0.31174 | 0.098177 | 0.26321 | 0.098177 | 0.26321 | 0 | 3.9145e-06 | 0 | -1.2401e-06 | 0 | -7.8262e-07 | 0 | -7.8262e-07
608 | 2 | 1 | 0.096934 | 0.31174 | 0.20971 | 0.65107 | 0.095381 | 0.23917 | 0.098177 | 0.26321 | 0 | -1.2401e-06 | 0 | 3.7032e-06 | 0 | -4.6087e-07 | 0 | -4.6087e-07
608 | 3 | 1 | 0.098177 | 0.26321 | 0.095381 | 0.23917 | 0.21214 | 0.643 | 0.098177 | 0.26321 | 0 | -7.8262e-07 | 0 | -4.6087e-07 | 0 | 3.5037e-06 | 0 | -4.6087e-07
608 | 4 | 1 | 0.098177 | 0.26321 | 0.095381 | 0.23917 | 0.098177 | 0.26321 | 0.21214 | 0.643 | 0 | -7.8262e-07 | 0 | -4.6087e-07 | 0 | -7.8262e-07 | 0 | 3.5037e-06

## Cfg_sq
cfg_n | r_ohm_per_km | x_ohm_per_km | r0_ohm_per_km | x0_ohm_per_km | c_nf_per_km | c0_nf_per_km | max_i_ka
101 | 3.06 | 0.101 | 12.24 | 0.404 | 1 | 1 | 0.052
102 | 1.117 | 0.41 | 4.468 | 1.64 | 1 | 1 | 0.105
103 | 3.06 | 0.095 | 12.24 | 0.38 | 1 | 1 | 0.046
104 | 1.16 | 0.082 | 4.64 | 0.328 | 1 | 1 | 0.096
105 | 1.16 | 0.082 | 4.64 | 0.328 | 1 | 1 | 0.085
106 | 0.387 | 0.078 | 2.589 | 0.321 | 1 | 1 | 0.18
107 | 1.16 | 0.08 | 4.64 | 0.32 | 1 | 1 | 0.085
108 | 1.14 | 0.112 | 4.56 | 0.448 | 1 | 1 | 0.085
109 | 1.16 | 0.08 | 4.64 | 0.32 | 1 | 1 | 0.085
110 | 0.195 | 0.07 | 1.368 | 0.28 | 1 | 1 | 0.258
1000 | 0.0001 | 0.0001 | 1000000 | 1000000 | 1 | 1 | 1

## Lines
from_bus | from_bus_terms | to_bus | to_bus_terms | std_type | length_km
2 | 1_2_3_4 | 3 | 1_2_3_4 | 1 | 0.07
3 | 1_2_3_4 | 4 | 1_2_3_4 | 1 | 0.035
4 | 1_2_3_4 | 5 | 1_2_3_4 | 1 | 0.07
5 | 1_2_3_4 | 6 | 1_2_3_4 | 1 | 0.105
6 | 1_2_3_4 | 7 | 1_2_3_4 | 1 | 0.035
3 | 1_2_3_4 | 8 | 1_2_3_4 | 4 | 0.03
4 | 1_2_3_4 | 9 | 1_2_3_4 | 2 | 0.105
9 | 1_2_3_4 | 10 | 1_2_3_4 | 3 | 0.03
5 | 1_2_3_4 | 11 | 1_2_3_4 | 6 | 0.03
6 | 1_2_3_4 | 12 | 1_2_3_4 | 4 | 0.03
7 | 1_2_3_4 | 13 | 1_2_3_4 | 5 | 0.03

## 3phTransformers
hv_bus | lv_bus | vn_hv_kv | vn_lv_kv | sn_mva | vk_percent | vkr_percent | pfe_kw | i0_percent | conn1 | conn2 | group | tap_step_percent | tap_pos | tap_max | tap_min | vrif_pu | db_percent | oltc_bus | r_ohm | x_ohm | synchro

## 1phTransformers
tr_n | circ_n | bus_n | from_ph | to_ph | vn_kv | sn_mva | vk_percent | vkr_percent | pfe_kw | i0_percent | tap_step_percent | tap_pos | tap_max | tap_min | vrif_pu | db_percent | oltc_bus | r_ohm | x_ohm | synchro
1 | 1 | 1 | 1 | 3 | 20 | 0.06667 | 4 | 1 | 0.06667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.5 | 2 | 0 | 0 | 1
1 | 2 | 1 | 2 | 1 | 20 | 0.06667 | 4 | 1 | 0.06667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.5 | 2 | 0 | 0 | 1
1 | 3 | 1 | 3 | 2 | 20 | 0.06667 | 4 | 1 | 0.06667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.5 | 2 | 0 | 0 | 1
1 | 1 | 2 | 1 | 0 | 0.23094 | 0.06667 | 4 | 1 | 0.06667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.5 | 2 | 0 | 0 | 1
1 | 2 | 2 | 2 | 0 | 0.23094 | 0.06667 | 4 | 1 | 0.06667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.5 | 2 | 0 | 0 | 1
1 | 3 | 2 | 3 | 0 | 0.23094 | 0.06667 | 4 | 1 | 0.06667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.5 | 2 | 0 | 0 | 1

## Loads
bus | from_ph | to_ph | p_mw | q_mvar | kzp | kip | kpp | kzq | kiq | kpq | type
8 | 1 | 4 | 0.008 | 0.0038746 | 0 | 0 | 1 | 0 | 0 | 1 | res
8 | 2 | 4 | 0.006 | 0.0029059 | 0 | 0 | 1 | 0 | 0 | 1 | ind
8 | 3 | 4 | 0.0035 | 0.0016951 | 0 | 0 | 1 | 0 | 0 | 1 | com
10 | 1 | 4 | 0.0195 | 0.0094443 | 0 | 0 | 1 | 0 | 0 | 1 | ind
10 | 2 | 4 | 0.0205 | 0.0099286 | 0 | 0 | 1 | 0 | 0 | 1 | ind
10 | 3 | 4 | 0.024 | 0.011624 | 0 | 0 | 1 | 0 | 0 | 1 | res
11 | 1 | 4 | 0.0125 | 0.006054 | 0 | 0 | 1 | 0 | 0 | 1 | com
11 | 2 | 4 | 0.0165 | 0.0079913 | 0 | 0 | 1 | 0 | 0 | 1 | com
11 | 3 | 4 | 0.014 | 0.0067805 | 0 | 0 | 1 | 0 | 0 | 1 | res
12 | 1 | 4 | 0.016 | 0.0077492 | 0 | 0 | 1 | 0 | 0 | 1 | ind
12 | 2 | 4 | 0.019 | 0.0092021 | 0 | 0 | 1 | 0 | 0 | 1 | res
12 | 3 | 4 | 0.0155 | 0.007507 | 0 | 0 | 1 | 0 | 0 | 1 | res
13 | 1 | 4 | 0.0035 | 0.0016951 | 0 | 0 | 1 | 0 | 0 | 1 | res
13 | 2 | 4 | 0.006 | 0.0029059 | 0 | 0 | 1 | 0 | 0 | 1 | com
13 | 3 | 4 | 0.008 | 0.0038746 | 0 | 0 | 1 | 0 | 0 | 1 | res

## Generators
bus | from_ph | to_ph | p_mw | q_mvar | kzp | kip | kpp | kzq | kiq | kpq | type | ref | v_ref_pu
1 | 1 | 4 | 100 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | cost | 1 | 1
1 | 2 | 4 | 100 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | cost | 1 | 1
1 | 3 | 4 | 100 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | cost | 1 | 1
8 | 2 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | pv | 0 | 0
10 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | pv | 0 | 0
10 | 2 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | pv | 0 | 0
10 | 3 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | pv | 0 | 0
11 | 2 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | pv | 0 | 0
12 | 1 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | pv | 0 | 0
13 | 3 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | pv | 0 | 0

## P_Profiles
id | cost | res | ind | com | pv
1 | 1 | 0.252 | 0.361 | 0.35 | 0
2 | 1 | 0.2395 | 0.402 | 0.3375 | 0
3 | 1 | 0.227 | 0.442 | 0.325 | 0
4 | 1 | 0.2145 | 0.425 | 0.3125 | 0
5 | 1 | 0.202 | 0.407 | 0.3 | 0
6 | 1 | 0.19675 | 0.413 | 0.295 | 0
7 | 1 | 0.1915 | 0.418 | 0.29 | 0
8 | 1 | 0.18625 | 0.445 | 0.285 | 0
9 | 1 | 0.181 | 0.472 | 0.28 | 0
10 | 1 | 0.18375 | 0.437 | 0.2925 | 0
11 | 1 | 0.1865 | 0.401 | 0.305 | 0
12 | 1 | 0.18925 | 0.456 | 0.3175 | 0
13 | 1 | 0.192 | 0.511 | 0.33 | 0
14 | 1 | 0.192 | 0.524 | 0.3425 | 0
15 | 1 | 0.192 | 0.537 | 0.355 | 0
16 | 1 | 0.192 | 0.58 | 0.3675 | 0
17 | 1 | 0.192 | 0.623 | 0.38 | 0
18 | 1 | 0.1995 | 0.609 | 0.41 | 0
19 | 1 | 0.207 | 0.595 | 0.44 | 0
20 | 1 | 0.2145 | 0.573 | 0.47 | 0
21 | 1 | 0.222 | 0.551 | 0.5 | 0
22 | 1 | 0.242 | 0.564 | 0.5625 | 0
23 | 1 | 0.262 | 0.576 | 0.625 | 0
24 | 1 | 0.282 | 0.631 | 0.6875 | 0
25 | 1 | 0.302 | 0.686 | 0.75 | 0
26 | 1 | 0.39025 | 0.686 | 0.7775 | 0
27 | 1 | 0.4785 | 0.685 | 0.805 | 0
28 | 1 | 0.56675 | 0.764 | 0.8325 | 0
29 | 1 | 0.655 | 0.842 | 0.86 | 0
30 | 1 | 0.68025 | 0.83 | 0.89 | 0
31 | 1 | 0.7055 | 0.818 | 0.92 | 0
32 | 1 | 0.73075 | 0.845 | 0.95 | 0
33 | 1 | 0.756 | 0.871 | 0.98 | 0
34 | 1 | 0.7435 | 0.878 | 0.9775 | 0.04925
35 | 1 | 0.731 | 0.884 | 0.975 | 0.0985
36 | 1 | 0.7185 | 0.868 | 0.9725 | 0.14775
37 | 1 | 0.706 | 0.851 | 0.97 | 0.197
38 | 1 | 0.68825 | 0.898 | 0.9575 | 0.289
39 | 1 | 0.6705 | 0.945 | 0.945 | 0.381
40 | 1 | 0.65275 | 0.922 | 0.9325 | 0.473
41 | 1 | 0.635 | 0.899 | 0.92 | 0.565
42 | 1 | 0.6275 | 0.895 | 0.89 | 0.5925
43 | 1 | 0.62 | 0.89 | 0.86 | 0.62
44 | 1 | 0.6125 | 0.855 | 0.83 | 0.6475
45 | 1 | 0.605 | 0.819 | 0.8 | 0.675
46 | 1 | 0.65025 | 0.821 | 0.8075 | 0.756
47 | 1 | 0.6955 | 0.823 | 0.815 | 0.837
48 | 1 | 0.74075 | 0.855 | 0.8225 | 0.918
49 | 1 | 0.786 | 0.886 | 0.83 | 0.999
50 | 1 | 0.771 | 0.895 | 0.835 | 0.9765
51 | 1 | 0.756 | 0.904 | 0.84 | 0.954
52 | 1 | 0.741 | 0.944 | 0.845 | 0.9315
53 | 1 | 0.726 | 0.984 | 0.85 | 0.909
54 | 1 | 0.69075 | 0.976 | 0.855 | 0.881
55 | 1 | 0.6555 | 0.968 | 0.86 | 0.853
56 | 1 | 0.62025 | 0.954 | 0.865 | 0.825
57 | 1 | 0.585 | 0.94 | 0.87 | 0.797
58 | 1 | 0.56475 | 0.959 | 0.8725 | 0.7135
59 | 1 | 0.5445 | 0.977 | 0.875 | 0.63
60 | 1 | 0.52425 | 0.981 | 0.8775 | 0.5465
61 | 1 | 0.504 | 0.984 | 0.88 | 0.463
62 | 1 | 0.4915 | 0.983 | 0.8475 | 0.389
63 | 1 | 0.479 | 0.982 | 0.815 | 0.315
64 | 1 | 0.4665 | 0.917 | 0.7825 | 0.241
65 | 1 | 0.454 | 0.851 | 0.75 | 0.167
66 | 1 | 0.517 | 0.858 | 0.6875 | 0.12525
67 | 1 | 0.58 | 0.865 | 0.625 | 0.0835
68 | 1 | 0.643 | 0.835 | 0.5625 | 0.04175
69 | 1 | 0.706 | 0.805 | 0.5 | 0
70 | 1 | 0.74375 | 0.815 | 0.4875 | 0
71 | 1 | 0.7815 | 0.824 | 0.475 | 0
72 | 1 | 0.81925 | 0.785 | 0.4625 | 0
73 | 1 | 0.857 | 0.745 | 0.45 | 0
74 | 1 | 0.8695 | 0.764 | 0.45 | 0
75 | 1 | 0.882 | 0.782 | 0.45 | 0
76 | 1 | 0.8945 | 0.733 | 0.45 | 0
77 | 1 | 0.907 | 0.684 | 0.45 | 0
78 | 1 | 0.887 | 0.657 | 0.4375 | 0
79 | 1 | 0.867 | 0.63 | 0.425 | 0
80 | 1 | 0.847 | 0.643 | 0.4125 | 0
81 | 1 | 0.827 | 0.655 | 0.4 | 0
82 | 1 | 0.80925 | 0.685 | 0.4 | 0
83 | 1 | 0.7915 | 0.714 | 0.4 | 0
84 | 1 | 0.77375 | 0.718 | 0.4 | 0
85 | 1 | 0.756 | 0.721 | 0.4 | 0
86 | 1 | 0.7435 | 0.717 | 0.395 | 0
87 | 1 | 0.731 | 0.712 | 0.39 | 0
88 | 1 | 0.7185 | 0.67 | 0.385 | 0
89 | 1 | 0.706 | 0.628 | 0.38 | 0
90 | 1 | 0.643 | 0.668 | 0.375 | 0
91 | 1 | 0.58 | 0.707 | 0.37 | 0
92 | 1 | 0.517 | 0.632 | 0.365 | 0
93 | 1 | 0.454 | 0.556 | 0.36 | 0
94 | 1 | 0.4035 | 0.529 | 0.3575 | 0
95 | 1 | 0.353 | 0.501 | 0.355 | 0
96 | 1 | 0.3025 | 0.431 | 0.3525 | 0
97 | 1 | 0.252 | 0.361 | 0.35 | 0

## Q_Profiles
id | cost | res | ind | com | pv
1 | 1 | 0.252 | 0.361 | 0.35 | 0
2 | 1 | 0.2395 | 0.402 | 0.3375 | 0
3 | 1 | 0.227 | 0.442 | 0.325 | 0
4 | 1 | 0.2145 | 0.425 | 0.3125 | 0
5 | 1 | 0.202 | 0.407 | 0.3 | 0
6 | 1 | 0.19675 | 0.413 | 0.295 | 0
7 | 1 | 0.1915 | 0.418 | 0.29 | 0
8 | 1 | 0.18625 | 0.445 | 0.285 | 0
9 | 1 | 0.181 | 0.472 | 0.28 | 0
10 | 1 | 0.18375 | 0.437 | 0.2925 | 0
11 | 1 | 0.1865 | 0.401 | 0.305 | 0
12 | 1 | 0.18925 | 0.456 | 0.3175 | 0
13 | 1 | 0.192 | 0.511 | 0.33 | 0
14 | 1 | 0.192 | 0.524 | 0.3425 | 0
15 | 1 | 0.192 | 0.537 | 0.355 | 0
16 | 1 | 0.192 | 0.58 | 0.3675 | 0
17 | 1 | 0.192 | 0.623 | 0.38 | 0
18 | 1 | 0.1995 | 0.609 | 0.41 | 0
19 | 1 | 0.207 | 0.595 | 0.44 | 0
20 | 1 | 0.2145 | 0.573 | 0.47 | 0
21 | 1 | 0.222 | 0.551 | 0.5 | 0
22 | 1 | 0.242 | 0.564 | 0.5625 | 0
23 | 1 | 0.262 | 0.576 | 0.625 | 0
24 | 1 | 0.282 | 0.631 | 0.6875 | 0
25 | 1 | 0.302 | 0.686 | 0.75 | 0
26 | 1 | 0.39025 | 0.686 | 0.7775 | 0
27 | 1 | 0.4785 | 0.685 | 0.805 | 0
28 | 1 | 0.56675 | 0.764 | 0.8325 | 0
29 | 1 | 0.655 | 0.842 | 0.86 | 0
30 | 1 | 0.68025 | 0.83 | 0.89 | 0
31 | 1 | 0.7055 | 0.818 | 0.92 | 0
32 | 1 | 0.73075 | 0.845 | 0.95 | 0
33 | 1 | 0.756 | 0.871 | 0.98 | 0
34 | 1 | 0.7435 | 0.878 | 0.9775 | 0.04925
35 | 1 | 0.731 | 0.884 | 0.975 | 0.0985
36 | 1 | 0.7185 | 0.868 | 0.9725 | 0.14775
37 | 1 | 0.706 | 0.851 | 0.97 | 0.197
38 | 1 | 0.68825 | 0.898 | 0.9575 | 0.289
39 | 1 | 0.6705 | 0.945 | 0.945 | 0.381
40 | 1 | 0.65275 | 0.922 | 0.9325 | 0.473
41 | 1 | 0.635 | 0.899 | 0.92 | 0.565
42 | 1 | 0.6275 | 0.895 | 0.89 | 0.5925
43 | 1 | 0.62 | 0.89 | 0.86 | 0.62
44 | 1 | 0.6125 | 0.855 | 0.83 | 0.6475
45 | 1 | 0.605 | 0.819 | 0.8 | 0.675
46 | 1 | 0.65025 | 0.821 | 0.8075 | 0.756
47 | 1 | 0.6955 | 0.823 | 0.815 | 0.837
48 | 1 | 0.74075 | 0.855 | 0.8225 | 0.918
49 | 1 | 0.786 | 0.886 | 0.83 | 0.999
50 | 1 | 0.771 | 0.895 | 0.835 | 0.9765
51 | 1 | 0.756 | 0.904 | 0.84 | 0.954
52 | 1 | 0.741 | 0.944 | 0.845 | 0.9315
53 | 1 | 0.726 | 0.984 | 0.85 | 0.909
54 | 1 | 0.69075 | 0.976 | 0.855 | 0.881
55 | 1 | 0.6555 | 0.968 | 0.86 | 0.853
56 | 1 | 0.62025 | 0.954 | 0.865 | 0.825
57 | 1 | 0.585 | 0.94 | 0.87 | 0.797
58 | 1 | 0.56475 | 0.959 | 0.8725 | 0.7135
59 | 1 | 0.5445 | 0.977 | 0.875 | 0.63
60 | 1 | 0.52425 | 0.981 | 0.8775 | 0.5465
61 | 1 | 0.504 | 0.984 | 0.88 | 0.463
62 | 1 | 0.4915 | 0.983 | 0.8475 | 0.389
63 | 1 | 0.479 | 0.982 | 0.815 | 0.315
64 | 1 | 0.4665 | 0.917 | 0.7825 | 0.241
65 | 1 | 0.454 | 0.851 | 0.75 | 0.167
66 | 1 | 0.517 | 0.858 | 0.6875 | 0.12525
67 | 1 | 0.58 | 0.865 | 0.625 | 0.0835
68 | 1 | 0.643 | 0.835 | 0.5625 | 0.04175
69 | 1 | 0.706 | 0.805 | 0.5 | 0
70 | 1 | 0.74375 | 0.815 | 0.4875 | 0
71 | 1 | 0.7815 | 0.824 | 0.475 | 0
72 | 1 | 0.81925 | 0.785 | 0.4625 | 0
73 | 1 | 0.857 | 0.745 | 0.45 | 0
74 | 1 | 0.8695 | 0.764 | 0.45 | 0
75 | 1 | 0.882 | 0.782 | 0.45 | 0
76 | 1 | 0.8945 | 0.733 | 0.45 | 0
77 | 1 | 0.907 | 0.684 | 0.45 | 0
78 | 1 | 0.887 | 0.657 | 0.4375 | 0
79 | 1 | 0.867 | 0.63 | 0.425 | 0
80 | 1 | 0.847 | 0.643 | 0.4125 | 0
81 | 1 | 0.827 | 0.655 | 0.4 | 0
82 | 1 | 0.80925 | 0.685 | 0.4 | 0
83 | 1 | 0.7915 | 0.714 | 0.4 | 0
84 | 1 | 0.77375 | 0.718 | 0.4 | 0
85 | 1 | 0.756 | 0.721 | 0.4 | 0
86 | 1 | 0.7435 | 0.717 | 0.395 | 0
87 | 1 | 0.731 | 0.712 | 0.39 | 0
88 | 1 | 0.7185 | 0.67 | 0.385 | 0
89 | 1 | 0.706 | 0.628 | 0.38 | 0
90 | 1 | 0.643 | 0.668 | 0.375 | 0
91 | 1 | 0.58 | 0.707 | 0.37 | 0
92 | 1 | 0.517 | 0.632 | 0.365 | 0
93 | 1 | 0.454 | 0.556 | 0.36 | 0
94 | 1 | 0.4035 | 0.529 | 0.3575 | 0
95 | 1 | 0.353 | 0.501 | 0.355 | 0
96 | 1 | 0.3025 | 0.431 | 0.3525 | 0
97 | 1 | 0.252 | 0.361 | 0.35 | 0